## Code Req
ATHERTON SUSTAINABILITY ATTRIBUTES - ELEMENTS/APPROACHES
Date: 09.7.2016
Category | ATTRIBUTE | EXTENT | Required by Cal Green | Required by Local Code | First Cost Low/Mod/ High | Net Zero | notes | Critical Date
ENERGY
Lighting
| Plug load controls | All offices and office support spaces within the buildings | Y | Y | N/A | N** | ** Not explicitly required for Net-zero, but makes achieving energy targets much easier and more cost effective | NA
Electrical | Daylight Dimming controls | Areas with access to windows or skylights | Y | Y | N/A | N** | ** Not explicitly required for Net-zero, but makes achieving energy targets much easier and more cost effective | NA
| Dimming controls | All other areas in the building | Y | Y | N/A | N** | ** Not explicitly required for Net-zero, but makes achieving energy targets much easier and more cost effective | NA
PV Ready | PV ready |  | Y | Y - PV ready per T24 | N/A for PV ready | Y | PV ready per T24, Energy Code, Section 110.10 | N/A
Commissioning | Commissioning of buildings during design and construction | all buildings over 50,000 square feet or "complex" mechanical systems | Y | Y | N/A | Y - verification of system performance | The proposed mechanical systems are all considered "complex" and will require commissioning input for Title 24. | NA
WATER
Stormwater Quality | Infiltration and Treatment BMPs (Raingardens, Flow-thru Planters, Pervious Paving). Reuse BMPs (Rainwater Reuse) | All improvements within limit of work | N | Y | N/A | Y | Treatment and Infiltration allows for groundwater exchange concept. Ecological Flows required by ILFI (match existing condition) | NA
Stormwater Quantity (rate) | Detention within Pervious Paving, Detention within Rainwater Cistern, Raingardens, Flow-thru Planters, | All improvements within limit of work | N | Y | N/A | Y | Ecological Flows required by ILFI (match existing condition) | NA

## SUSTAINABILTY MATRIX
ATHERTON SUSTAINABILITY ATTRIBUTES - ELEMENTS/APPROACHES
CATEGORY | ATTRIBUTE | EXTENT | SUSTAINABILITY SCORECARD NOTES | ROI LIBRARY | ROI ADMIN PD | EDUCATIONAL ASSETS | RESILIENCY | OPPORTUNITIES | BASE BID ESTIMATED COST $,000 | ALTERNATE ESTIMATED COST $,000
ENERGY
Lighting
Electrical | Energy Monitoring | Each panelboard and large piece of equipment | Important for net-zero to verify energy usage and production and to identify problem areas of high energy use for reduction | TBD | Immediate | Potential to educate community as well as city staff. Can be displayed on dynamic screen - production of PVs coupled with energy demand. Has proven to contribute to user responsibility and increased energy savings. |  | Ability to track usage and ensure system is working efficiently. Saves operational costs | Library $16 | CH $13
| Solar Emergency Microgrid | Police Station-Solar PV; energy storage; and monitoring, communications & control SEM to provide indefinite back-up power for critical loads | Adds additional level of redundancy for power outages, reduces reliance on fossil fuels in the event that trucks cannot get through to deliver fuel (or in the event that fuel is prioritized for places like hospitals and it is difficult to get in time), provides opportunity to use the police station as a safe refuge where community members can come to charge phones and get in touch with loved ones during a major emergency Space for batteries is currently not included in building layout. | TBD | TBD | Leadership role in community. | renewable source for emergencies; may reduce generator size | First civic center to include technology; showcase for SValley |  | Library: $604K; PD: $422K; Admin/PD/Chambers: $770K
PVs | PVs | Exterior Roof | PV system can reduce size of Emergency Generator. | Approx. 5 years | Depending on amount 5-10 years | leadership role for community; Potential to educate community as well as city staff. Can be displayed on dynamic screen - production of PVs coupled with energy demand. Has proven to contribute to user responsibility and increased energy savings. | ZNE: provides renewable source of power; | First ZNE civic center | Library : $573K | ADMIN/PD: $2.42M
Mechanical
Geo Exchange | Water Source Heat Pumps | Geothermal field with ~45 wells. | Water source heat pumps provide excellent energy efficiency. Any alternate mechanical system would need to reach the efficiency of this system. 24 years expected Payback if the geoexchange will displace PV (i.e. we are included the initial cost reduction of PV to get to ZNE). This ROI assumes no cost of money and a 6% inflation in energy rates per annum. | CAMPUS benefit approx. 24 years | See Library | Leadership Opportunity. Ties Water story to Energy Story |  |  |  | CH $581 Lib $193
Chilled Water Thermal Storage Tanks | Demand based electrical reduction and reduced energy use | Central Plant | Underground thermal storage tank to store chilled water. Allows the campus to make and store cooling water in the evening and get heat recovery from the heat pumps when the rest of the occupied spaces (police) are in heating. It also reduced PG&E demand charges and allows cooling when the outside air temperature is cooler, making the equipment more efficient and less noise during occupied periods. Drawback: Acoustical in the evening. | CAMPUS benefit approx. 5 years | See Library | Contributes to Water Story |  |  |  | 98
Energy Monitoring | Measurement of building systems by end use | Campus wide | Important for net-zero to verify energy usage and production and to identify problem areas of high energy use for reduction. You cannot manage what you don't measure. | NA | NA | Potential to educate community as well as city staff. Can be displayed on dynamic screen - production of PVs coupled with energy demand. Has proven to contribute to user responsibility and increased energy savings. Contributes to achieving ZNE results |  | Provides ability to track system performance and save on potential operational costs | Lib $40
Central Plant | Efficient system for campus approach | Campus wide | Each building in the facility is served by a central chilled and hot water plant. The plant consists of a modular heat pump chiller which provides both heating and cooling from the single unit. The modular nature of the system allows it to operate at peak efficiency, regardless of load. | CAMPUS | App. 0 yrs | Potential to educate community as well as city staff. Can be displayed on dynamic screen - production of PVs coupled with energy demand. Has proven to contribute to user responsibility and increased energy savings. Contributes to achieving ZNE results |  | Provides ability to track system performance and save on potential operational costs | Lib $40
Water
On-site Well | Well with power source and pressure tank for onsite non-potable demands | One well for entire site | Well allows for groundwater exchange concept (offset withdrawals with onsite infiltration). Base Cost: - Hook irrigation system and building up to municipal water supply. Well Alternate Additional Cost: - TOTAL COST = $89,000 Estimated ROI: - Water savings: 83,439 gal/yr at Library and 600,000 gal/yr for site irrigation (+ 2M gal for irrigation system start up) at $.01/gal. - Savings Year 1&2 = $21,669 - ROI = ($89,000 - $21,669)/$6,834/yr = 10 years -ROI (irrigation only) = ($89,000 - $20,000)/$6,000 = 11.5 years | CAMPUS benefit -10-11 years for both Library and CO/PD | See Library | Enhances water balance story. Water from well is used for irrigation and goes back to replenish aquifer | Resiliency from water price increase and water shortage |  |  | 89
Graywater | Treatment for Passive Irrigation | At Library | Reduces reliance on well for irrigation. CAC raised concerns that graywater could be harmful to redwoods if proper soaps are not used in bathrooms for handwashing or if children wash paint brushes in bathroom sinks. Some operational controls required to ensure potentially harmful chemicals are not used in the library sinks. Base Cost: - Plumb library bathroom sinks directly to sewer. Graywater Alternate Additional Cost: - TOTAL COST = $42,000 Estimated ROI: - Assumes 10,000 gal of water savings per year at $0.01/gal. ($100/yr) - ROI = ($42,000 / $100/yr) = 420 yrs | CAMPUS benefit - app. 420 yrs | See Library | N | Resiliency from water price increase and water shortage | First civic center to include rainwater for full Water Reuse Story; showcase for SValley |  | Lib $42
Rainwater Harvesting | Treatment for reuse as irrigation and/or toilet flushing | Collection and reuse at Library Building. Tie collection system for Police / Admin Bldg. into Library treatment and reuse system. | Meets stormwater management objectives. Reduces reliance on municipal water for toilet flushing and irrigation. If rainwater harvesting is not implemented additional bio retention area is needed for stormwater treatment and detention. Base Cost: - 400 sq ft of raingarden including deep base rock section to provide necessary detention. Rainwater Harvesting Alternate Additional Cost: - Total = $231,000 Estimated ROI: - Assumes 15,000 gal of water savings per year at $0.01/gal. ($150/yr) - ROI = ($231,000)/$150/yr = 1,540 yrs | CAMPUS benefit - app. 1540 yrs | See Library | Part of the Water Story; illustration of Atherton as a Steward | Not dependent of municipal systems | First civic center to include rainwater for full Water Reuse Story; showcase for Svalley |  | 48
Additional Stormwater Infiltration | Underground storage for permeability and compliance | site water | Prioritizes infiltration into soils rather than storage and release to Atherton channel. Improves flood risk. Supports aquifer exchange concept. Base Cost: - Below grade storage for detention (assume buried pipe or chamber system). SW Infiltration Alternate Additional Cost: - Cost = $57,490 Estimated ROI: - NA. No annual savings from this strategy. | NA | NA | Part of the Water Story; illustration of Atherton as a Steward; allows civic center to demonstrate alternative products and approaches. |  | Contributes to Water Story |  | 43
Blackwater | Treatment for unconditional reuse | All building wastewater | City Council rejected: Reduces reliance on well for irrigation / flushing. Requires additional room for equipment and plumbing fixtures to be provided with dual connections. | M | M | N
Dual Plumbing | Dual plumb library building such that non-potable water can be used for flushing toilets | Library Building and Potentially Police / Admin Bldg. | Net zero requires no potable water to be used for non-potable demands. Base Cost: - Plumb library building and police/admin building with municipal domestic water only. Dual Plumbing Alternate Additional Cost: LIBRARY: - Cost = $13,000 POLICE BUILDING - Cost = $28,000 Estimated ROI: LIBRARY - Assumes 15,000 gal of water savings per year at $0.01/gal. ($150/yr) - ROI = ($13,000/$150/yr) = 87 yrs POLICE / ADMIN BUILDING - Assumes 69,000 gal of water savings per year at $0.01/gal. ($690/yr) - ROI = ($28,000/$690/yr) = 40 yrs | App. 87 yrs | App. 40 yrs | Part of the Water Story; illustration of Atherton as a Steward | Plan for alternative water source | Combine with Well water for enhanced water story |  | CH $28 Lib $13
Well + Dual Plumbing Combined | Combined costs / ROI for Well and Dual plumbing at library building and police/admin building such that non-potable water can be used for flushing toilets | Campus wide | Net zero requires no potable water to be used for non-potable demands. Base Cost: - Plumb library building and police/admin building with municipal domestic water only. Well and Dual Plumbing Alternate Additional Cost: - Cost = $130,000 Estimated ROI: - Water savings: 83,439 gal/yr at Library and 600,000 gal/yr for site irrigation (+ 2M gal for irrigation system start up) at $.01/gal. - Savings Year 1&2 = $21,669 - ROI = ($130,000 - $21,669)/$6,834/yr = 16 years | CAMPUS benefit -app. 16 yrs | See Library | Enhances water balance story. Water from well is used for potable uses, recycled water for in building use |  | Contributes to Water Story; ROI improved |  | $130K
Well + Dual Plumbing + Stormwater Infiltration Combined | Combined costs / ROI for Well, Stormwater Infiltration, Dual plumbing at library building and police/admin building such that non-potable water can be used for flushing toilets | Campus wide | Net zero requires no potable water to be used for non-potable demands. Base Cost: - Plumb library building and police/admin building with municipal domestic water only. Well, Infiltration and Dual Plumbing Alternate Additional Cost: - Cost = $187,490 Estimated ROI: - Water savings: 83,439 gal/yr at Library and 600,000 gal/yr for site irrigation (+ 2M gal for irrigation system start up) at $.01/gal. - Savings Year 1&2 = $21,669 - ROI = ($187,490 - $21,669)/$6,834/yr = 24 years | CAMPUS benefit - app 24 yrs. | See Library | Enhances water balance story. Water from well is used for irrigation and goes back to replenish aquifer |  | Contributes to Water Story |  | $187K
Plumbing
Solar Thermal | Solar thermal heating | Located at Police Building to support showers only | Solar thermal systems will work to preheat domestic hot water and reduce the energy needed to heat the buildings. ROI – Plumb-1: Solar Thermal for Police Station showers – expected ROI details as follows: 7 year payback after receipt of California Solar Rebate. | App. 7 yrs | App. 7 yrs | Displays how some PV is used for building energy and some hot water use. Water and Energy connection |  | Contributes to Water Story |  | PD $53
Architectural
Envelope | Good insulated walls and roofs | Library Building and Police / Admin Bldg. | New civic center and library: 2x6 metal stud wall with R-19 batt insulation and 1” of rigid insulation (U-0.071, R-14.1 overall) At historic council chambers: 2x4 wood stud wall with R-15 batt insulation (U-0.083, R-12 overall) Civic center and Historic building: Pitched roof with R-30 insulation at ceiling (U-0.032, R-31.25) Library: flat roof with R-30 insulation (U-0.032, R-31.25) Solarban 72 low-e double pane glazing (U-0.40, SHGC-0.30, VLT 70%) | App. 0 yrs | App. 0 yrs | Reduces demand on electrical and mechanical systems | Assists in providing comfort a if power should go out | Contributes to Energy Story |  | PD $53
Glazing | High efficiency glazing as part of architectural envelope | Library Building and Police / Admin Bldg. | Solar thermal systems will work to preheat domestic hot water and reduce the energy needed to heat the buildings. ROI – Plumb-1: Solar Thermal for Police Station showers – expected ROI details as follows: 7 year payback after receipt of California Solar Rebate. | App. 0 yrs | App. 0 yrs | Reduces demand on electrical and mechanical systems |  | Contributes to Energy Story |  | PD $53
Lighting type | Reduced Light Power Density (LPD) | Library Building and Police / Admin Bldg. | An aggressive yet achievable building average lighting power density (LPD) target of 0.65 W/ft2 is assumed for the project. All regularly occupied spaces are simulated as having daylight responsive controls, which continuously adjust the electric light output in response to available daylight. The controls are continuous dimming with a 50 FC set point. Exterior lighting is estimated at 0.05 w/sf, for a total of 2,000 watts. – expected ROI details as follows: immediate payback 7 year payback after receipt of California Solar Rebate. | App. 0 yrs | App. 0 yrs | Reduces demand on mechanical systems; increases indoor environmental quality |  | Contributes to Indoor Environmental Quality |  | PD $53
Windows | Good occupant satisfaction | Library Building and Police / Admin Bldg. | Solar thermal systems will work to preheat domestic hot water and reduce the energy needed to heat the buildings. ROI – Plumb-1: Solar Thermal for Police Station showers – expected ROI details as follows: | App. 0 yrs | App. 0 yrs | User comfort | assists in providing comfort and ventilation if power should go out | Contributes to Indoor Environmental Quality |  | PD $53
Ceiling Fans | Good occupant satisfaction | Library Building and Police / Admin Bldg. | HV Ceiling Fans provide user comfort and satisfaction while increasing the temperature band by as much as 3 degrees | App. 0 yrs | App. 0 yrs | User comfort |  | Contributes to Water Story |  | PD $53