## Slide 1
Craig Lewis
Executive Director
Clean Coalition
650-796-2353 mobile
craig@clean-coalition.org
20 Jul 2021
Solar Microgrids & Community Microgrids
Unparalleled energy resilience

## Slide 2: Clean Coalition (nonprofit)
Mission
To accelerate the transition to renewable energy and a modern grid through
technical, policy, and project development expertise.
100% renewable energy end-game
  25% local, interconnected within the distribution grid and facilitating resilience without dependence on the transmission grid.
  75% remote, dependent on the transmission grid for serving loads.
Notes: 2

## Slide 3: Natural gas infrastructure is not resilient
Assertion: Gas-driven generation is often claimed to be resilient.
Reality: Gas infrastructure is not resilient and takes much longer to restore than electricity infrastructure.
Threats: Gas infrastructure can be flat-out dangerous and is highly vulnerable to earthquakes, fires, landslides, and terrorism.
Chart: Service Restoration Timeframes (M7.9 Earthquake)
| 1 day | 2 days | 3 days | 1 week | 2 weeks | 3 weeks | 1 month | 2 months | 3 months | 6 months
Gas | 0 | 0 | 0 | 0 | 2.5 | 5 | 10 | 30 | 65 | 100
Electricity | 5 | 25 | 60 | 95 | 97 | 98.5 | 100 | 100 | 100 | 100
Source: The City and County of San Francisco Lifelines Study
2010 San Bruno Pipeline Explosion

## Slide 4: Value-of-resilience (VOR) depends on tier of load
Everyone understands there is significant value to resilience provided by indefinite renewables-driven backup power, especially for the most critical loads
  But, nobody has quantified this value of unparalleled resilience.
  Hence, there is a substantial economic gap for renewables-driven microgrids.
The Clean Coalition aims to establish a standardized value-of-resilience (VOR) for critical, priority, and discretionary loads that will help everyone understand that premiums are appropriate for indefinite renewables-driven backup power to critical loads and almost constant backup power to priority loads, which yields a configuration that delivers backup power to all loads a lot of the time
The Clean Coalition’s VOR approach aims to standardize resilience values for three tiers of loads:
  Tier 1 are mission-critical & life-sustaining loads and warrant 100% resilience. Tier 1 loads usually represent about 10% of the total load.
  Tier 2 are priority loads that should be maintained as long as long as doing so does not threaten the ability to maintain Tier 1 loads. Tier 2 loads usually represent about 15% of the total load.
  Tier 3 are discretionary loads make up the remaining loads, usually about 75% of the total load. Maintained when doing so does not threaten Tier 1 & 2 resilience.

## Slide 5: Percentage of time online for Tier 1, 2, and 3 loads for a Solar Microgrid designed for the University of California Santa Barbara (UCSB) with enough solar to achieve net zero and 200 kWh of energy storage per 100 kW solar.
Chart: 
| 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
Column1
Percentage of total load
Percentage of time
Tier 3 = Discretionary load, ~75% of total load
Tier 1 = Critical, life-sustaining load, ~10% of total load
Tier 2 = Priority load, ~15% of total load
Typical load tier resilience from a Solar Microgrid

## Slide 6: A typical diesel generator is configured to maintain 25% of the normal load for two days. If diesel fuel cannot be resupplied within two days, goodbye. This is hardly a solution for increasingly necessary long-term resilience. In California, Solar Microgrids provide a vastly superior trifecta of economic, environmental, and resilience benefits.
Chart: 
| 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
Column1
Percentage of total load
Percentage of time
Tier 3 = Discretionary load, ~75% of total load
Tier 1 = Critical, life-sustaining load, ~10% of total load
Tier 2 = Priority load, ~15% of total load
Diesel generators are designed for limited resilience

## Slide 7: GLP Community Microgrid case study
Goleta Load Pocket (GLP)
Community Microgrid
case study

## Slide 8: Goleta Load Pocket (GLP) and attaining resilience
The GLP is the perfect opportunity for a comprehensive Community Microgrid
GLP spans 70 miles of California coastline, from Point Conception to Lake Casitas, encompassing the cities of Goleta, Santa Barbara (including Montecito), and Carpinteria.
GLP is highly transmission-vulnerable and disaster-prone (fire, landslide, earthquake).
200 megawatts (MW) of solar and 400 megawatt-hours (MWh) of energy storage will provide 100% protection to GLP against a complete transmission outage (“N-2 event”).
  200 MW of solar is equivalent to about 5 times the amount of solar currently deployed in the GLP and represents about 25% of the energy mix.
  Multi-GWs of solar siting opportunity exists on commercial-scale built environments like parking lots, parking structures, and rooftops; and 200 MW represents about 7% of the technical siting potential.
  Other resources like energy efficiency, demand response, and offshore wind can significantly reduce solar+storage requirements.

## Slide 9: Target 66kV feeder at the core of the GLP
Legend
16kV Gladiola Feeder
Substations
16kV Gaucho Feeder
16kV Professor Feeder
University of California Santa Barbara (UCSB)
Santa Barbara Airport
Tier 3 Fire Threat
Tier 2 Fire Threat
220 kV Transmission
66 kV Feeder #4311
Sanitary or Water Districts
Goleta Substation
Goleta Water District West
Isla Vista Substation
Vegas Substation
UCSB

## Slide 10: Target 66kV feeder serves critical GLP loads
Legend
16kV Gladiola Feeder
Substations
16kV Gaucho Feeder
16kV Professor Feeder
University of California Santa Barbara
Santa Barbara Airport
Tier 3 Fire Threat
220 kV Transmission
66 kV Feeder #4311
Fire Stations
Sanitary or Water Districts
Proposed 160-240 MWh Battery
Goleta Valley Cottage Hospital
Direct Relief
Fire Station # 17
Direct Relief
Vegas Substation
Isla Vista Substation
Proposed 160-240 MWh Battery
Fire Station # 8
Goleta Sanitary District
Deckers
UCSB
SB Airport

## Slide 11: Target 66kV feeder grid area block diagram
Isla Vista Substation (66-to-16kV)
Fire Station #17
66kV underground interconnection
Vegas Substation (66-to-16kV)
UCSB
+ Solar
SBA (runway lights & ATC)
Direct Relief
+ Solar Microgrid
SBA (Main Terminal)
Goleta Sanitary District
Goleta Substation (220-to-66kV)
Diagram Elements
66 kV Distribution Feeder #4311
16 kV Gladiola Feeder
16 kV Gaucho Feeder
16 kV Professor Feeder
Planned 160-240 MWh Battery
Grid isolation switch (open, closed)
Smart meter switch (open, closed)
Fire Station #8
66kV distribution feeder #4311 with multiple branches
Deckers
+ Solar Microgrid
Tier 2 & 3 facilities
Tier 2 & 3 facilities
Tier 2 & 3 facilities
160+ MWh battery
Goleta Substation has eight feeders, all 66kV, that serve the entire GLP
Tier 2 & 3 facilities

## Slide 12: SBUSD Solar Microgrids case study
Santa Barbara Unified School District (SBUSD)
case study

## Slide 13: Santa Barbara Unified School District (SBUSD)
The entire Santa Barbara region is surrounded by extreme fire risk (earthquake & landslide risk too) and is extremely vulnerable to electricity grid outages.
The SBUSD is a major school district that increasingly recognizes the value-of-resilience (VOR) and has embraced the Clean Coalition’s vision to implement Solar Microgrids at a number of its key schools and other critical facilities.
SMHS is in the middle of the extensive SBUSD service area.

## Slide 14: Six SBUSD Solar Microgrid sites

## Slide 15: Guaranteed SBUSD bill savings and free VOR

## Slide 16: San Marcos High School (SMHS) case study
San Marcos High School (SMHS)
case study

## Slide 17: SMHS is vulnerable to distribution outages too

## Slide 18: San Marcos High School (SMHS)
SMHS is a large public high school serving 2,000+ students in grades 9 through 12.
Red Cross designated facility.
School features include:
  Array of classroom buildings
  Large pool
  Gymnasium
  Football stadium
  Multiple baseball fields
  Cafeteria
  Outdoor Greek theater
  Auditorium
  Numerous tennis & basketball courts
Craig Lewis in the Class of 1981.

## Slide 19: SMHS Solar Microgrid overview
The SMHS Solar Microgrid is intended to enable the school to operate independently during grid outages of any duration with indefinite resilience for the most critical loads and resilience for all loads for significant percentages of time.
Solar
  725 kWp
  Solar is entirely in the form of solar parking canopies
  Net Zero Energy (NZE) is exceeded at 101%
Battery Energy Storage System (BESS)
  700 kWh energy capacity
  350 kW power capacity
Critical (Tier 1) loads
  Food service refrigerators & freezers, maintained indefinitely
  4.36 kW of average load
  3.44% of total average load
Priority (Tier 2) loads
  Gym lights and Main Distribution Frame, maintained at least 80% of the time
  4.32 kW of average load
  3.41% of total average load

## Slide 20: San Marcos High School – site layout

## Slide 21: Solar Microgrids coming to Camarillo CCFs
Solar Microgrids coming to Camarillo Critical Community Facilities (CCFs)

## Slide 22: Solar Microgrids targeted for 5 Camarillo CCFs
Police Station
Library
City Hall
Corp Yard
Wastewater Treatment Plant
Notes: This map shows an overview of the City of Camarillo with respect to each of the sites included in this microgrid feasibility Study
Total of 5 sites:
Police Station
Library
City Hall
Corp Yard
WWT
Detailed views of proposed new resource locations (solar and storage)will be shown later for each site.